| module 1200 | Installation Manual |
| --- | --- |
| ABKM keypad |  |

Installation

1) Before you install this equipment, please read this full manual.

Programming

LED indicators

Remove

1   2   3

4   5   6

7  8 9

- 0   #

Hinge front door

- Remove the top two security screws as shown. Do NOT remove the bottom screws.

The front door will hinge downwards to allow access for mounting holes and connection terminals.

Note: The protective film on the front of the intercom should not be removed until fully installed.

- Use appropriate wall fixings. 8-10mm anchors, 75mm deep with M5 screw are recommended as a minimum.

|  |  |  |  |  |  |  |  | ON when incorrect codes entered and outputs are locked out. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  | GREEN when output 1 activated. |
|  |  |  |  |  |  |  |  |  | RED when output 2 activated. |
| 1 | 2 | 3 |  |  |  |  |  |  |  |  |  |  |  |  |  | FAST FLASHING – Wrong code entered / error. |
| 4 | 5 | 6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | SLOW FLASHING - in normal standby mode. |
| 7 | 8 | 9 |  |  |  |  |  |  |  |  |  |  |  |  |  | ON in programming mode. |
| * | 0 | # |  |  |  |  |  |  |  |  |  |  |  |  |  | ON when relay 3 activated. |

Note: Programming can only begin 60 seconds after power on.

Enter Programming mode

The unit is now in programming mode. Amber LED

0	0	0	0	*	*	will remain ON. 0000 is default programmers code.

Note: Pressing ** again will exit programming

mode.

Enter new programmers code

| 0 |  | 1 |  | ? |  | ? |  | ? |  | ? |  | # |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Side View

Wiring

- Carefully follow the wiring instructions. Additional wiring suggestions for electric strike lock and magnetic lock are shown below.

|  | Tamper |  | INT Lock |  |
| --- | --- | --- | --- | --- |
|  |  | N/C |  | O/P 1 inhib |  |
|  | OUT2 |  |  | Sense | Advanced |
|  | Relay |  |  | (-)GND | Keypad |
|  | Select | N/C N/O |  | DU out | functions |
|  |  | N/O |  | K or A |  |
|  | OUT3 | COM |  |  |  |
|  |  | N/C |  |  |  |
|  | + - |  |  |  |  |
| 12v | N/CCOMN/CN/O | I/OData | egress |  |
| power |  | N/O |  |  |  |
| adaptor |  |  |  |  |  |
| 12-24v | OUT1 OUT2 |  |  |
| dc |  |  |  |  |  |

Example Strike lock wiring

|  | A/C |
| --- | --- |
|  | PSU for |
|  | lock |
| EGR | Strike |
| Keypad |  |
|  | lock |
| module |  |
|  | Exit Button |
| N/O |  |
| COM |  |
| N/C | Break |
| - | Glass |
| + | N/O |

| 12-24v dc | Optional emergency |
| --- | --- |
|  | break glass unit |

Example DC Magnetic lock wiring

|  |  |  | D/C |  |
| --- | --- | --- | --- | --- |
|  |  | Recommend | PSU for | Magnetic |
|  |  |  | lock | Lock |
|  |  | diode fitted |  |  |
| EGR |  | here |  |  |
|  | Exit Button |  |  |  |
| N/O |  |  |  |  |
| COM |  |  |  |  |
| N/C |  |  |  | Break |
| + |  |  |  | Glass |
| - |  |  |  | N/C |
|  | 12-24v dc |  | Optional emergency |
|  |  |  |  | break glass unit |

|  | Location |  | 4-8 digit code |  |  |  | Validate |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Record or Delete user codes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 1 |  |  | 0 |  |  |  | 2 |  |  |  |  | 0 |  | 0 |  | 0 |  |  |  |  | ? |  | ? |  |  | ? |  |  | ? |  |  |  |  | # |  |  |
| 10= relay 1 codes |  |  | 2= add code | Memory locations |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (1000 available) |  |  | 5= delete code | 000-999 for relay 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20= relay 2 codes |  |  |  |  |  |  |  |  |  |  | 001-100 for relay 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Pin code 4-8 digits | Validate |
| (100 available) |  |  |  |  |  |  |  |  |  |  | 001-100 for relay 3 |  |  |

30= relay 3 codes

(100 available)

Example: Add user 31 to have access code 5555 operating relay 2….

|  | 2 | 0 |  |  |  | 2 |  |  |  |  |  |  |  | 0 |  |  |  | 3 |  |  |  |  | 1 |  |  |  |  |  | 5 |  |  |  | 5 |  |  |  | 5 |  | 5 |  |  |  |  | # |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Group 2 |  | Add code |  |  | Location 31 |  |  |  |  |  |  |  |  |  | Pin code 5555 |  |  |  |  |  | Validate |
| Delete a code |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ? | ? |  |  |  | 5 |  |  |  |  |  |  |  | ? |  |  |  | ? |  |  |  |  | ? |  |  |  |  |  | # |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10=relay1 |  |  |  |
|  |  | 20=relay2 | Delete code |  | ID location to be deleted |  |  | Validate |  |  |  |  |  |  |  |  |  |  |  |
| 30=relay3 |
| Delete all codes in a group |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | ? | ? |  |  | 0 |  |  | 9 |  |  | 9 |  |  |  |  | 9 |  |  |  |  | # |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10=relay1 group |  |  |
|  | 20=relay2 group |  |  |  |  |  | Super delete code |  |  |  |  |  |  | Validate |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 30=relay3 group |
|  | Programming Relay output times & modes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | ? | ? |  |  |  |  |  | 0 |  |  |  | or |  | 1 |  | - | 9 |  |  | 9 |  |  |  | 9 |  |  |  | 9 |  | 9 |  |  |  | # |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 = start / stop toggle mode (latching) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 51=relay1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Validate |
|  |  | 52=relay2 |  |  |  |  |  |  |  |  |  |  |  |  | 1-99999 = seconds momentary operation |  |  |  |  |  |

53=relay3

Programming SUPER user code

Super user code is an optional feature which allows the same code to operate outputs 1, 2 or 3.

|  | 0 |  | 2 |  |  | ? |  |  | ? |  |  | ? |  | ? |  |  | # |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Location |  |  |  |  |  | 4-8 digit code |  |  |  | Validate |
| Using super user code |  |  |  |  |  |  |  |  |  |
|  | ? |  | ? |  | ? |  |  | ? |  |  |  | # |  |  | 1 |  | Activate output 1 |
|  | ? |  | ? |  | ? |  |  | ? |  |  |  | # |  |  | 2 |  | Activate output 2 |
|  | ? |  | ? |  | ? |  |  | ? |  |  |  | # |  |  | 3 |  | Activate output 3 |

User Instructions

Using standard user code

To use standard code, simply enter the 4 digit code. You do not need to press any other digits.

Note: Remember to exit programming mode with ** before testing user codes.

Using super user code

| ? |  | ? |  | ? |  | ? |  | # |  | 1 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ? |  | ? |  | ? |  | ? |  | # |  | 2 |
| ? |  | ? |  | ? |  | ? |  | # |  | 3 |

Activate output 1

Activate output 2

Activate output 3

Advanced Features

Restoring defaults

While in programming mode, enter the following to delete all codes and settings apart from the

Master code.. (this can take up to 2.5 minutes)...

| 9 |  | 9 |  | 9 |  | 9 |  | # |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

When the master code is forgotten….

- Wire a push button (or replicate with wire link) across the EG IN terminal and (-)GND.

- Switch off power for 1 minute.

- Switch ON power.

- during the first 60 seconds, press the EG button once to enable the function.

- Enter the following code..

| 8 |  | 0 |  | 8 |  | 0 |  | * |  | * |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

The keypad should now be in programming mode, ready to accept new data.

Additional keypad information – Note: These features are not commonly used.

EG IN (EGRESS INPUT)

Connect a push button between this terminal and (-)GND. When Egress button is pressed, output 1 will be activated for the programmed delay. Egress button is usually located inside a building and used as a push to exit.

K or A. (KEYPAD ACTIVE OUTPUT)

An NPN transistor open collector output. It switches to (-) ground for 10 seconds on each key touching. This can be used to turn on lights, CCTV camera, or buzzer to notify a guard. The rating of this output is: Ic max: 100mA sink, Vc max: 24VDC

DU OUT (DURESS OUTPUT)

An NPN transistor open collector output. It switches to (-) ground after the Duress Code is entered. Use it to trigger an alarm zone, or turn on a buzzer to notify a guard. Ic max: 100mA sink. Vc max: 24VDC

DOOR SENSE

N/C connected to (-)GND, to be connected to a normally closed door contact. It can be used to

generate a door open alarm or door forced open alarm.

O/P 1 Inhibit

Normally open. When closed, this disables all codes for relay group 1 except super user and duress codes.

Interlock Output

NPN transistor output, open collector, max power 24v dc, 100mA sink. Used to operate a door in conjunction with another keypad, or prevent two doors being opened at the same time.

Tamper N/C

Normally closed tamper switch. This can be used in conjunction with a tamper switch on a box or enclosure to prevent tampering. This can be connected to an alarm system.

DATA I/O PORT (Data Communication Bus) The Data I/O port is prepared for setting up a data bus for the connection of the auxiliary reader-keypads and the split-decoder in system expansion